## Slide 1: RCSD Anita B. Smith Water Treatment Plant Pump Optimization
RCSD Staff
March 4, 2026
1

## Slide 2: Project Overview
Rubidoux Community Services District energy efficiency project
Modernization of pumping system at the Anita B. Smith Water Treatment Facility
Eliminate redundant booster pumping infrastructure
Install high-efficiency pumps, motors, and Variable Frequency Drives (VFDs)
Convert system from two-stage pumping to single-stage pumping
Maintain full treatment and regulatory compliance

## Slide 3
Air stripper originally installed for historical VOC treatment
VOCs have not been detected in source water for decades
Granular Activated Carbon (GAC) treatment remains in place
GAC can adsorb many organic contaminants if they reappear
Treatment barriers remain in place to maintain water quality

## Slide 5
4
Well #4
(1100 GPM)
100HP US Motor No VFD
Well #6
(2200 GPM)
200HP US Motor No VFD
GAC
GAC
AIR STRIPPER
CURRENT PROCESS FLOW CHART
BOOSTER #1 (200HP)
BOOSTER #2 (200HP) Back-up
BOOSTER #3 (100HP)
6
IX Bypass
(43 PSI)
(48 PSI)
(48 PSI)
(36 PSI)
(80-90 PSI) Depending on Tank Levels
After both IX processes (19 PSI) Due to elevation of inlet on Air Stripping Tower

## Slide 6: Current Typical Operating Pumping Load
Well Pumps
• Well 6 – 200 HP • Well 4 – 100 HP
Booster Pumps (Lead/Lag Operation)
• 200 HP Lead Booster • 100 HP Lag Booster
Typical Operating Load
≈ 600 HP
(Additional 200 HP booster maintained as standby redundancy)

## Slide 7: Proposed Pumping Configuration
The project will:
• Remove the air stripper from normal operation
• Eliminate the booster pumping station
• Install new pumps sized for system pressure
• Install VFDs on both Well 6 and Well 4
• Deliver treated water directly to the distribution system
This converts the facility to single-stage pumping.

## Slide 8
4
6
Well #4
(1100 GPM)
150HP US Motor, (or whatever HP deemed necessary), VFD and new pump to accommodate additional head pressure
GAC
GAC
AIR STRIPPER
PROPOSED PROCESS FLOW CHART
BOOSTER #1 (200HP) with VFD to Manage AS Level
BOOSTER #2 (200HP)
BOOSTER #3 (100HP)
(80-90 PSI) Depending on Tank Levels
(48 PSI)
(48 PSI)
(43 PSI)
(36 PSI)
(19 PSI) Due to elevation of inlet on Air Stripping Tower
Well #6
(2200 GPM)
250HP US Motor (or whatever HP deemed necessary), VFD and new pump to accommodate additional head pressure
IX Bypass
Air Stripper and Boosters no longer necessary in this operational scenario

## Slide 9: Before vs After Energy Comparison
Current Typical Operation
Wells:
4 - 100 HP
6 - 200 HP
Booster Pumps
1-100 HP
2-200 HP
3-200 HP
Total: ≈ 600 HP + 200 HP Backup = 800HP to maintain for the life cycle of the treatment plant
Proposed Operation
Wells Only (VFD controlled)
4 - 150 HP
6 - 300 HP
Total: ≈ 450 HP
Estimated Reduction ≈ 200 HP
• Estimated ~600,000 – 900,000 kWh per year energy savings
• Reduced operating cost and electrical demand
• Improved energy efficiency for municipal water delivery

## Slide 10: Project Benefits
• Eliminates booster pumping infrastructure
• Reduces energy consumption and electrical demand
• Simplifies plant hydraulics and operations
• Improves pressure control using VFD technology
• Modernizes water infrastructure

## Slide 11: Well 18 Failure