## Slide 2
4
Well #4
(1100 GPM)
100HP US Motor No VFD
Well #6
(2200 GPM)
200HP US Motor No VFD
GAC
GAC
AIR STRIPPER
CURRENT PROCESS FLOW CHART
BOOSTER #1 (200HP)
BOOSTER #2 (200HP) Back-up
BOOSTER #3 (100HP)
6
IX Bypass
(43 PSI)
(48 PSI)
(48 PSI)
(36 PSI)
(80-90 PSI) Depending on Tank Levels
After both IX processes (19 PSI) Due to elevation of inlet on Air Stripping Tower

## Slide 4
4
6
Well #4
(1100 GPM)
150HP US Motor, (or whatever HP deemed necessary), VFD and new pump to accommodate additional head pressure
GAC
GAC
AIR STRIPPER
PROPOSED PROCESS FLOW CHART
BOOSTER #1 (200HP) with VFD to Manage AS Level
BOOSTER #2 (200HP)
BOOSTER #3 (100HP)
(80-90 PSI) Depending on Tank Levels
(48 PSI)
(48 PSI)
(43 PSI)
(36 PSI)
(19 PSI) Due to elevation of inlet on Air Stripping Tower
Well #6
(2200 GPM)
300HP US Motor, VFD and new pump to accommodate additional head pressure
IX Bypass
Air Stripper and Boosters no longer necessary in this operational scenario

## Slide 5: Before vs After Comparison
Previous Operation
Two-Stage Pumping System
• Well 4 → 100 HP
• Well 6 → 200 HP
• Booster Pumps → 500 HP Total
Total Operating Load
≈ 600 HP + 200 HP Backup Booster
Total Installed Infrastructure≈ 800 HP
• Higher energy demand
• Increased maintenance
• Complex operation
Modernized • Simplified • Efficient
New Operation
Single-Stage VFD Controlled System
• Well 4 → 150 HP
• Well 6 → 300 HP
Total Operating Load
≈ 450 HP
Benefits
• Significant energy savings
• Reduced maintenance requirements
• Reduction from 5 pumps and motors down to 2

## Slide 6
Well 4 fully rehabilitated and returned to service
New pump and motor installed at Well 4
New piping installed to allow operation without boosters

## Slide 7
Brine tank cleaned and reloaded with new salt
New actuated blend valve installed for raw/treated water control
21 valves and actuators replaced on nitrate treatment system
New pH, conductivity, and process flow instrumentation installed
Well 4 and Well 6 GAC media replaced and ready for service
Instrumentation and communications room installed

## Slide 9: Well 6 Rehabilitation Update
Well 6 has been pulled
Pre-rehabilitation downhole video inspection completed 5/20
Initial inspection confirms rehabilitation work can proceed 5/22
Upcoming work cleaning, rehabilitation
Post-rehabilitation downhole video inspection
Installation and Start up of new Well Equipment

## Slide 10: Site Security & Perimeter Improvements
16-camera security system fully installed and operational
New Perimeter alarms installed. New monitoring company hired
Block wall and wrought iron fencing installation will begin this 5/27

## Slide 13: Remaining Project Items
Installation of new water softener system
Installation of new plant effluent flow meter
Asphalt and concrete repair and replacement in construction areas
Painting removal and final surface cleanup
Complete Well 6 rehabilitation and reinstall with new pump and motor equipment
Continue SCADA and instrumentation improvements
Brine Line Cleaning
Beautification

## Slide 14: Team Recognition
Project success has required coordination between ALL District Departments
The Smith Plant rehabilitation represents a major investment in RCSD infrastructure
Thank you to all staff involved for the continued effort and commitment to the project
The work completed will improve reliability, resiliency, efficiency, and long-term sustainability

## Slide 15: Questions????